Drinking Water Quality and Compliance

The Water Security Agency and the Ministry of Environment requires that at least once each year waterworks owners provide notification to consumers of the quality of water produced and supplied as well as information on the performance of the waterworks in submitting samples as required by a Minister’s Order or Permit to Operate a waterworks.  The following is a summary of the Town of Pilot Butte’s water quality and sample submission compliance record for the year of 2022.  This report was completed on 17-Jan-2022.  Readers should refer to Water Security Agency’s “Municipal Drinking Water Quality Monitoring Guidelines, June 2015, EPB 502” for more information on minimum sample submission requirements.  Permit requirements for a specific waterworks may require more sampling than outlined in the department’s monitoring guidelines.  If consumers need more information on the nature and significance of specific water tests, for example, “what is the significance of selenium in a water supply”, more detailed information is available from:

http://www.hc-sc.gc.ca/ewh-semt/pubs/water-eau/index_e.html .

Water Quality Standards

Bacteriological Quality

Regular Samples	Regular Samples	# of Positive Regular

Parameter/Location	Limit	Required	Submitted	Submitted (Percentage)

Total Coliform	0 Organisms/100 mg/L	      _____52_____	_____52_______	________0_____________

E. coli			   0 Organisms/100 ml		          _____52_____	_____52_______	________0_____________

Background Bacteria	Less than 200 Organisms/100 mL	_____52_____	_____52_______	________0_____________

The owner/operator is responsible to ensure that 100 per cent of all bacteriological samples are submitted as required.  All waterworks are required to submit samples for bacteriological water quality; the frequency of monitoring depends on the population served by the waterworks.

# Water Disinfection

# Chlorine Residual in Distribution System for Test Results Submitted with Bacteriological Samples

## Minimum	Free Chlorine	Total Chlorine	# Tests	# Tests	# Adequate

Parameter	Limit (mg/L)	Residual Range	Residual Range	Required	Submitted	Chlorine (Percentage)

Chlorine	0.1 mg/L free OR

Residual	0.5 mg/L total	____0.08-0.92____	____0.26-0.96__	____52___	___52____	_____52_______ (100%)

A minimum of 0.1 milligrams per litre (mg/L) free chlorine residual OR 0.5 mg/L total chlorine residual is required at all times throughout the distribution system unless otherwise approved.  A proper chlorine submission is defined as a bacteriological sample submission form with both the free and total chlorine residual fields filled out.  An adequate chlorine is a result that indicates that the chlorine level is above the regulated minimums.  An adequate chlorine may be counted even if the chlorine results were submitted incorrectly.  A waterworks is required to submit chlorine residual test results on every bacteriological sample they submit.

Water Disinfection

Free Chlorine Residual for Water Entering Distribution System from Waterworks Records-From Water Treatment Plant Records_______________

Parameter	Limit (mg/L)	Test Level Range	# Tests Performed	# Tests Not Meeting Requirements

Free Chlorine Residual	at least 0.1	_____0.22-0.84___	______365______	____________0__________________

A minimum of 0.1 milligrams per litre (mg/L) free chlorine residual is required for water entering the distribution system.  Tests are normally performed on a daily basis by the waterworks operator and are to be recorded in operation records.  This data includes the number of free chlorine residual tests performed, the overall range of free chlorine residual (highest and lowest recorded values) and the number of tests and percentage of results not meeting the minimum requirement of 0.1 mg/L free chlorine residual.

Turbidity – From Water Treatment Plant Records

Limit	Test Level	# Tests Not Meeting	Maximum	# Tests	# Tests

Parameter	(NTU)	Range	Requirements	Turbidity (NTU)	Required	Performed

Turbidity	__1.0___	0.03-0.89	______0__________	_____0.89_____	___Continuous__	____Continuous___

Turbidity is a measure of water treatment efficiency.  Turbidity measures the “clarity” of the drinking water and is generally reported in Nephelometric Turbidity Units (NTU).  All waterworks are required to monitor turbidity at the water treatment plant.  The frequency of measurement varies from daily for small systems to continuous for larger waterworks.

# Chemical – Health Category

## Limit	Limit	Sample	# Samples	# Samples	# Samples

## Parameter	MAC (mg/L)	IMAC (mg/L)	Results	Exceeding MAC/IMAC	Required	Submitted

Arsenic	0.010		_0.0012	________0____________	____1_____	_____1________

Barium	1.0		 0.0014	________0____________	____1_____	_____1________

Boron		5.0	__0.1__	________0____________	____1_____	_____1________

Cadmium	0.005		<0.00015	________0____________	____1_____	_____1________

Chromium	0.05		<0.00019	________0____________	____1_____	_____1________

Fluoride (avg.*)	1.5		__<0.05	________0____________	____1_____	_____1________

Lead	0.01		0.00007	________0____________	____1_____	_____1________

Nitrate (avg.*)	45.0		__<0.2_	________0____________	____1_____	_____1________

Selenium	0.01		<0.00113	________0____________	____1_____	_____1________

Uranium	0.02		 0.00040_	________0____________	____1_____	_____1________

Substances within the chemical health category may be naturally occurring in drinking water sources or may be the result of human activities.  These substances may represent a long-term health risk if the Maximum Acceptable Concentration (MAC) or Interim Maximum Acceptable Concentration (IMAC) is exceeded.  All drinking water supplies are required to monitor for substances in the Chemical-Health category, the frequency of monitoring depends on the population served by the waterworks.  Some waterworks will add fluoride to drinking water as a means to aid in the prevention of dental decay.

# General Chemical

## Aesthetic		Sample	# Samples	# Samples

Parameter	Objectives* (mg/L)	Results (average)	Required	Submitted

Alkalinity	500		____40.3______	____1______	____1_______

Bicarbonate	No Objective		____49________	____1______	____1_______

Calcium	No Objective		_____6_______ 	____1______		____1_______

Carbonate	No Objective		______0_______	____1______		____1_______

Chloride	250		_____1.1______		____1______		____1_______

Conductivity	No Objective		_____111_______	____1_______		____1_______

Hardness	800	______27_______	____1_______	____1_______

Magnesium	200	_____0.02_______		____1_______ 	____1_______

PH	No Objective		_____7.8______ 		____1_______ 	 ____1______

Sodium	300		______12______ 	____1_______ 		____1_______

Sulphate	500		______11.4_____ 	____1_______ 		____1_______

Total dissolved solids      1500		_____84_______		____1_______ 		____1_______

All waterworks serving less than 5000 persons are required to submit water samples for SE’s General Chemical category once every two years if a ground water source or once per three months every second year if a surface water or blended surface/groundwater source.  The General Chemical category includes analysis for alkalinity, bicarbonate, calcium, carbonate, chloride, conductivity, hardness (as CaCO3), magnesium, sodium, sulphate and total dissolved solids.

The last sample for General Chemical analysis was submitted on 18-Jan-2022.  Sample results indicated that there were no exceedences of the provincial aesthetic objectives for the General Chemical category.

*Objectives apply to certain characteristics of or substances found in water for human consumptive or hygienic use.  The presence of these substances will affect the acceptance of water by consumers and/or interfere with the practice of supplying good quality water.  Compliance with drinking water aesthetic objectives is not mandatory as these objectives are in the range where they do not constitute a health hazards.  The aesthetic objectives for several parameters (including hardness as CaCO3, magnesium, sodium and total dissolved solids) consider regional differences in drinking water sources and quality.

More information on water quality and sample submission performance may be obtained from:

Town of Pilot Butte

222 Diamond Place, Pilot Butte

S0G 3Z0

(306) 781-4547